EU Solis tech hotline +34 919 495 286

Transient response :

It is much slower when the battery DC/DC is operating, whether charging or discharging.

Feedback:

There seem to be two feedback paths: one via the EPM and one via the Self-Use logic.

Meter Placement: Grid, choice of smartmeter :

https://diysolarforum.com/threads/solis-switch-off-transient.88767/#post-1177523

“Eastron SDM120” is polled every 2 seconds and has no ringing. Response is slow due to the longer polling interval.

“Acrel 3 Phase” is polled every 1 seconds and has no ringing.

“Acrel 1 Phase” is polled every second
- When the inverter is hitting the battery : always has ringing.
- When battery is inactive, it is fast and reacts almost instantly after polling.

Hunch: what if the inverter battery control loop runs on a 2 seconds period, so the SDM120 actually uses the correct 2 seconds period, but... the Eastron is queried every second so... what if there's a bug and it adds the values and thus gets double the correct reading? Multiplying the open loop gain by 2 sure would reduce the phase margin.

→ Applying gain 0.5 on meter reading with Acrel solves all ringing issues
→ Special cases needed for PV only and to limit export (so it doesn’t double)

Comparison between two Acrel meters, 1 phase with fix versus 3 phase:
- Battery: identical, but 3 phase is simpler
-

Meter Placement: Load, choice of smartmeter :

“Eastron SDM120” is polled every 2 seconds, works fine, quick response.

“Acrel 3 Phase” is polled every 1 seconds, works fine, slow smoothed response.

2024-08-15 10:20	Test with constant meter reading of 500W, battery charging.
Inverter output power remains around 500W average but fluctuates a lot depending on PV power as internal battery charger takes time to catch up with PV production.

“Acrel 1 Phase” is polled every second, does not work at all.

About EPM :

EPM OFF, FailSafe OFF, Meter ON

It still uses meter data to control export

EPM OFF, FailSafe OFF, Meter OFF

No sun : battery discharge and export power remain constant to the same value they had when turned off.

→ EPM only controls export limit for zero export when lots of PV power is available. It doesn’t control the actual output power of the inverter. This is probably in the meter logic.

Battery Limits

43130	Battery Charge Power Limit
43131	Battery Discharge Power Limit

Power saving

Battery below minimum SOC: 12W

Cut off grid, backup port off
PV charges battery.
Without PV, power from battery 12W (with display backlight on)

Cut off meter communication → Safe mode
PV is shutdown, no battery charging
Power from battery 12W (with display backlight on)
Grid port power: SDM120 displays 0

Banque de registres intéressants vers adresse 46000, 45900, 45500
écriture interdite

43717 writable contains battery current in 0.1A units (access denied)